PART 1- GENERAL

PART 1-GENERAL

  - SCOPE

The work covered by this specification consists of furnishing all labor, equipment, materials and accessories, and performing all operations required for the correct installation of polyolefin flexible closed cell insulation for indoor or outdoor duct wrap applications. The installation guidelines outlined in this document are Nomaco recommendations and are intended to ensure a successful installation. Any variations other than what is supported by this document may cause unwanted side effects and compromise the purpose and design of the insulation.

1.2	REFERENCES

- ASTM C 177			Thermal Conductivity (k) by Guarded Hot Plate Apparatus

- ASTM C 335			Thermal Conductivity (k) for Pipe Insulation

- ASTM C 411			Upper Temperature Limit

- ASTM C 518			Thermal Conductivity (k) by Heat Flow Meter Apparatus

- ASTM C 1427		Standard Specifications for Preformed Flexible Cellular Polyolefin Foam Insulation

- ASTM D 1622		Density

- ASTM D 3575		Density

- ASTM E 84			Surface Burning Characteristics

- ASTM E 96			Water Vapor Transmission

1.3	QUALITY ASSURANCE

- Insulation materials will be manufactured under a strict quality control program assuring quality product delivered to the job site.  Insulation material that has become damaged shall not be installed.

- Workmanship:  all insulation to be installed by a qualified applicator and applied in accordance with the manufacturer’s recommendations.

- All work shall comply with all applicable federal, state and local codes and laws.  This shall include, but shall not be limited to, the Occupational Safety and Health Act.

- All work shall conform to accepted industry and trade standards for commercial and industrial insulation.

- Surfaces to be insulated shall be cleaned free of dirt, scale, moisture, oil and grease.

1.4	DELIVERY AND STORAGE OF MATERIALS

- Deliver all materials to the job site and protect the insulation from dirt, water, chemical and mechanical damage before, during and after installation.  Damaged insulation shall not be installed and it shall be removed from the project site.

- Deliver insulation, and where applicable, coverings, cements, adhesives, coatings, etc. to the site in factory supplied containers with the manufacturer’s stamp or label affixed showing warning statement, name of manufacturer and brand.

- Storage and transport of materials should utilize the manufacturers’ carton, original shipment packaging, or approved white reflective packaging. Damage to the insulation may result from improper packaging.

PART 2- PRODUCTS

2.1	NOMACO POLYOLEFIN INSULATION

- Products must be manufactured by Nomaco and identified by their container with one of the following trade names:  IMCOSHEET, NOMAPLY, THERMA-CEL SHEET.

- Any material submitted claiming to be a similar, like, or equal must demonstrate (meet or exceed) the same physical characteristics as Nomaco manufactured insulation (i.e., flexible, non-porous, and non-fibrous).  In addition, materials must meet the following criteria:

- Material shall have a density ranging from 1.5 to 1.8 lb/ft3 (ASTM D 1622, ASTM 3575).

- Material must have a maximum thermal conductivity (k) of 0.25 Btu-in/hr-ft2-(F @ 75(F mean temperature (ASTM C 518, ASTM C 177).

- Material must have a maximum Water Vapor Transmission rate of 0.00 Perm-in (ASTM E 96, Desiccant Method).

- Material up to 1” thick, when tested in accordance with ASTM E 84, shall have a flame spread rating not greater than 25 and a smoke developed rating not greater than 50.

2.2	SHEET INSULATION

- IMCOSHEET, NOMAPLY, THERMA-CEL SHEET: black-pigmented insulation in sheet form. See appropriate price sheet for available dimensions, standard thicknesses and configurations.

BLACK SHEET TO BE INSTALLED INDOORS ONLY.

- IMCOSHEET, NOMAPLY, THERMA-CEL SHEET:  same as above but white-pigmented.

WHITE SHEET TO BE INSTALLED INDOORS OR OUTDOORS.

2.3	ACCESSORIES

- 320 Contact Adhesive:  standard air-drying contact adhesive (brush, roller, or spray applied) formulated for joining sheet insulation seams and adhering sheet insulation to duct substrate. 320 is tan / beige when dry.

- 620 Contact Adhesive: same as above, but black when dry.

2.4	JACKETING

A jacket or coating is NOT required for INDOOR applications (installations NOT exposed to direct sunlight or weather elements), but is optional for indoor applications depending upon the anticipated service conditions.  A coating (see COATINGS below) is required (jacket material is optional) for OUTDOOR applications exposed either to direct sunlight or weather elements.

2.5	ADHESIVES

The adhesives below have been identified as having excellent adhesion to any rough surface of polyolefin closed cell flexible foam insulation.

- Field applied Contact Adhesives.  Because of the unacceptable performance of some adhesive systems, please refer to Technical Information Bulletin for a list of recommended adhesives to be used in conjunction with therma-cel sheet.

ENGINEERING NOTES:

- The recommended contact adhesives are all subject to specific service temperature ranges. The contact adhesive manufacturer should be contacted to verify correct application for service temperatures anticipated.  (The contact adhesive, when applied on joints or when applied between layers of insulation is not exposed to the extreme temperatures experienced by the reactor or piping.  Therefore, the design temperature of the adhesive will be much less demanding and must be estimated)

- It is very important that contact adhesive be allowed to flash fully prior to joining two impermeable substrates such as polyolefin insulation and sheet metal. Contact adhesive will not continue to flash under an impermeable substrate and therefore, will not set up properly.

- The flash time of a contact adhesive is dependent upon relative humidity and temperature. Relatively speaking, the lower the  temperature or the higher the relative humidity, the longer the time required for the contact adhesive to fully flash.

- A contact adhesive will be slightly tacky, yet dry to the touch when fully flashed.

2.6	COATINGS

- Insulation MUST be coated (jacket is optional) in OUTDOOR applications exposed either to direct sunlight or weather elements.  All of the coatings below are solvent-based mastics and will provide the necessary protection from direct sunlight or weather elements when applied per the coating manufacturer’s installation guidelines.  The surface of the insulation must be clean and free of any dust, dirt, scale, moisture, oil and grease.  Because of the unacceptable performance of some coating systems, please refer to Technical Information Bulletin TA6 for a list of recommended coatings to be used in conjunction with polyolefin insulation.

ENGINEERING NOTES:

- After long term outdoor exposure, the above coatings may weather to a light tan or yellow color.  This surface appearance will not affect any other physical properties of the coating.

- The flexibility, impermeance, and chemical inertness of polyolefin insulation prevent strong adherence of water based latex paints. Therefore, water based latex paints are NOT recommended for coating polyolefin insulation where physical abuse is possible.

- The recommended coatings are all subject to specific application and service temperatures. The manufacturer should be contacted to verify correct utilization for anticipated temperatures.

- In some indoor applications a particular color is desired. Consult the coating manufacturer about available pigment additives. OUTDOOR applications should NOT be pigmented.

PART 3- EXECUTION

3.1	WORKMANSHIP

Installation shall be performed by a qualified insulation contractor who specializes in industrial and/or commercial mechanical systems.

3.2	INSTALLATION

3.2.1	GENERAL RECOMMENDATIONS AND CONSIDERATIONS

- For best results, high quality materials, tools, and equipment should be used including, but not limited to:

- Sufficiently sized work table

- Straight edge

- Sharp knife

- Hand roller

- 320 or 620 Adhesive (see section 2.3, 2.5)

- Coatings (see section 2.6)

ENGINEERING NOTES:

A. Mechanical pins/fasteners are limited to the ”Weld” and “Grip” versions. Pins/fasteners of the “Peel and Stick” version are not allowed (The Pressure Sensitive Adhesive of Peel & Stick pins/fasteners may fail under anticipated stresses).

- Polyolefin insulation must be coated or jacketed for protection from sunlight and the elements when being used in outdoor applications.  The application of a jacket or coating to indoor installations is optional.

- All surfaces must be clean and free of any dust, dirt, scale, moisture, oil and grease before applying adhesives or coatings.  Do not apply insulation to wet or frosted surfaces.  Any instructions regarding surface preparation for a particular manufacturer’s adhesive or coating should be followed.

- Polyolefin sheet insulation is manufactured with one rough (non-skin) side and one smooth skin side.  Adhesive should be applied to both the rough side of the insulation (100% coverage) and the duct (100% coverage).  Rough side of sheet must be bonded to the duct.

- Polyolefin sheet must be adhered to the duct using mechanical fasteners/pins (in addition to adhesive) on a minimum of 24” centers (see ENGINEERING NOTE 3.2.1 paragraph A and Drawing 1).

- Never stretch polyolefin insulation to cover the surface of the duct.  Rather it is preferable to cut insulation ¼” longer than the duct and adhere it to the duct under slight compression.  This will provide tight fitting joints.

- Care should be taken to insure that all joints are sealed properly.  Poorly sealed joints may result in undesired heat loss or condensation.

- Seams and butt joints should be staggered if multiple layers are applied. The smooth surface of polyolefin sheet should be mechanically “roughed” when adhering multiple layers.

- Circulation of air helps prevent condensation.  Consideration should be given during the design stage to provide adequate space between the duct and other objects to provide air movement.

- Compression of insulation thickness reduces thermal efficiencies.  Consideration should be given during the design stage to provide adequate support to minimize or eliminate compression of the insulation.

3.2.2	SPECIFIC GUIDELINES FOR INSTALLING POLYOLEFIN SHEET ON DUCTWORK

- Measure Polyolefin Sheet:  Each dimension of the sheet should be sized ¼” longer than the corresponding dimension of duct to be covered.  This allows the sheet to be installed in compression and insures tight fitting joints.

- Cut Polyolefin Sheet:  Sheet should be laid out flat on a work table.  Smooth, straight cuts can be accomplished by using a straight edge and a sharp knife.

- Sequence to Size and Install Polyolefin Sheet:  Sheet should be installed using a watershed technique.  Pieces should be cut (remember to cut each piece ¼” longer than the measured duct dimension) and installed in the following sequence (see drawing 1):

- Cut the bottom piece first.  The width measurement of the sheet should be the same width as the duct plus 1/4”.

- Next, cut the two side pieces.  The height measurement of each side piece should include the thickness of the bottom sheet plus 1/4”.  The top edge of the insulation should be kept flush with the top of the duct.

- Finally, cut the top sheet.  The width measurement of the top piece should include the wall thickness of both side pieces plus 1/4”.

DRAWING 1

- Apply Adhesive:  Following the adhesive manufacture’s instructions, apply 320 or 620 adhesive (for acceptable alternative adhesives refer to section 2.5, paragraphs A) in the following sequence:

- Brush, roller, or spray coat 100% coverage of contact adhesive on the metal duct surface;

- Brush, roller, or spray coat 100% coverage of contact adhesive to the rough (non-skin) side of the polyolefin sheet leaving a ½” wide uncoated border at butt-edge seams;

- Allow the contact adhesive to dry to the touch before bonding the polyolefin sheet to the duct.

- Bond Polyolefin Sheet to the Duct:  Sheet should be adhered to the duct such that it is slightly  compressed as follows:

- Position the sheet so that it overlaps both edges of the duct equally (by 1/8”);

- Lightly hold the sheet in this position and spot adhere it in the center by applying pressure;

- Compress the butt edges of the sheet into place (flush with edge of duct) and adhere by applying pressure;

- Adhere the remainder of the sheet by applying even pressure.  Care should be taken to prevent trapping air pockets.  A small hand roller may be helpful in distributing pressure across the entire surface area.

- Apply Mechanical Fasteners:  Apply mechanical fasteners/pins (minimum of 24” centers, see ENGINEERING NOTE 3.2.1 paragraph A and Drawing 1 or 3).

- Seal Seams/Butt Joints:  Spread the seam or joint and with a small brush, apply contact adhesive to both butt edges.

- Insulate Standing Seams:  Standing seams shall be insulated by adhering thin strips of polyolefin sheet.  Adhesive should always be applied to the rough (non-skin) surface of the sheet.  If adhesive must be applied to small sections of the smooth side (skin) of the sheet, a wire brush should be used for field roughing the surface.

- Insulate Standing Seams (Alternate Method):  Standing seams may also be insulated using mitered half sections of polyolefin pipe insulation.  Mitering the ends of the half sections will help insure a tight fit, resulting in an air tight system.  The wall thickness of the half sections should be equal to the wall thickness of sheet used to insulate the duct surface.

- Apply Weather Barrier Coating:  Sheet must be coated (jacketing is optional) for protection from sunlight and weather elements when used in outdoor applications (see section 2.6 for recommended coatings).

3.2.3	ALTERNATIVE METHOD FOR MEASURING, CUTTING, AND INSTALLING POLYOLEFIN SHEET ON DUCTWORK

- Measurement and Cutting of Polyolefin Sheets:  The sheet may be sized and cut in a single piece that folds around the circumference of the duct.  Each width (w) and height (h) measurement should be ¼” larger than the respective duct measurement.  Three of the corners are produced by cutting V-grooves one thickness (t) wide and half the thickness (½ t) into the polyolefin sheet (see Drawing 2).  Following the watershed method, the fourth corner should be located at the bottom of the duct (see Drawing 3) and is produced by cutting one of the side sections (h + t) to overlap the bottom section of insulation (see Drawing 2).

DRAWING 2

DRAWING 3

- Installation of Polyolefin Sheets:  Follow these steps from section 3.2.2 to complete the installation

- Apply Adhesive (3.2.2-D);

- Bond Sheet to the Duct (3.2.2-E);

- Apply Mechanical Fasteners (3.2.2-F);

- Seal Seams/Butt Joints (3.2.2-G);

- Insulate Standing Seams (3.2.2-H);

- Apply Weather Barrier Coating, if applicable (3.2.2-I).

3.3	COATING AND JACKET INSTALLATION

For outdoor applications when insulation is exposed to direct sunlight or weather elements application of a weather barrier coating is required (jacket is optional; see sections 2.4 and 2.6).  The surface of the insulation must be clean and free of any dust, dirt, scale, moisture, oil and grease. It is recommended that a layer of mesh reinforcement (fiber scrim; see coating manufacturer’s guidelines) be incorporated into any coating system application to provide the required mechanical integrity. Follow coating or jacket manufacturer’s application instructions/guidelines.

# Text boxes

Specification for:

Nomaco All Brands

Polyethylene Insulation

Page 1 of 6 (March 2016)

CSI, 3-Part Specification

Sheet Insulation

Indoor & Outdoor

Wrap for Ducts

Mechanical fasteners

(minimum 24” centers)

(c)

(b)

(b)

(a)

Mechanical fasteners (minimum 24” centers)

½ t

t

t

t

w

w

h

h + t