# PART 1- GENERAL

# 1.1	SCOPE

The work covered by this specification consists of furnishing all labor, equipment, materials and accessories, and performing all operations required for the correct installation of flexible closed cell Polyolefin Insulation for applications on chilled water piping systems. The installation guidelines outlined in this document are Nomaco recommendations and are intended to ensure a successful installation. Any variations other than what is supported by this document may cause unwanted side effects and compromise the purpose and design of the insulation.

# 1.2	REFERENCES

- ASTM C177			Thermal Conductivity (k) by Guarded Hot Plate Apparatus

- ASTM C335			Thermal Conductivity (k) for Pipe Insulation

- ASTM C411			Upper Temperature Limit

- ASTM C518			Thermal Conductivity (k) by Heat Flow Meter Apparatus

- ASTM C1427			Standard Specifications for Preformed Flexible Cellular Polyolefin Foam Insulation

- ASTM D1622			Density

- ASTM D3575			Density

- ASTM E84			Surface Burning Characteristics

- ASTM E96			Water Vapor Permeability

# 1.3	QUALITY ASSURANCE

- Insulation materials shall be manufactured under a strict quality control program assuring quality product delivered to the job site.  Insulation material that has become damaged shall not be installed.

- Workmanship:  all insulation to be installed by a qualified applicator and applied in accordance with the manufacturer’s recommendations.

- All work shall comply with all applicable federal, state and local codes and laws.  This shall include, but shall not be limited to, the Occupational Safety and Health Act.

- All work shall conform to accepted industry and trade standards for commercial and industrial insulation.

- Surfaces to be insulated shall be cleaned free of dirt, scale, moisture, oil and grease.

# 1.4	DELIVERY AND STORAGE OF MATERIALS

- Deliver all materials to the job site and protect the insulation from dirt, water, chemical and mechanical damage before, during and after installation.  Damaged insulation shall not be installed and it shall be removed from the project site.

- Deliver insulation, and where applicable, coverings, cements, adhesives, coatings, etc. to the site in factory supplied containers with the manufacturer’s stamp or label affixed showing warning statement, name of manufacturer and brand.

- Storage and transport of materials should utilize the manufacturer’s carton, original shipment packaging, or approved white reflective packaging. Damage to the insulation may result from improper packaging.

# PART 2- PRODUCTS

# NOMACO POLYOLEFIN INSULATION

- Products must be manufactured by Nomaco and identified by their container with one of the following trade names: IMCOLOCK, ARCTICFLEX, NOMALOCK, THERMA-CEL.

- Pipe (tubular) insulation must display the ASTM E84 (25/50) flame spread and smoke developed ratings.  Any material submitted claiming to be a similar, like, or equal must demonstrate (meet or exceed) the same physical characteristics as Nomaco manufactured insulation (i.e., pre-slit/pre-glued products, non-porous, and non-fibrous).  In addition, materials must meet the following criteria:

- Material shall have a density ranging from 1.5 to 1.8 lb/ft3 (ASTM D1622).

- Material must have a maximum thermal conductivity (k) of 0.25 Btu-in/hr-ft2-(F @ 75(F mean temperature (ASTM C518, ASTM C177 or ASTM C335).

- Material must have a maximum Water Vapor Transmission rate of 0.00 Perm-in (ASTM E96, Desiccant Method).

- Material up to 1” thick, when tested in accordance with ASTM E84, shall have a flame spread rating not greater than 25 and a smoke developed rating not greater than 50.

# PIPE INSULATION

- IMCOLOCK, NOMALOCK, THERMA-CEL (tubular): black-pigmented, longitudinally pre-slit tubular pipe insulation with closure system consisting of pressure sensitive adhesive and protective release tape applied at the factory.  Allows precision-cut angles and pre-cut pieces to be joined by the application of industry standard contact adhesives.  See appropriate price list for available tube and pipe sizes, standard wall thicknesses, and lengths.

- ARCTICFLEX (tubular): same as above, but white pigmented.

# 2.3	     SHEET INSULATION

- NOMAPLY, IMCOSHEET, THERMA-CEL SHEET: black or white-pigmented insulation in sheet form.  See appropriate price list for available dimensions, standard thicknesses, configurations.

# ACCESSORIES

- R-320 and R-620 Contact Adhesive:  standard air-drying contact adhesive (brush or roller applied) formulated for adhering mitered and circumferential (butt) joints of polyolefin insulation. R-320 is beige / tan colored. R-620 is black colored.

- 720 LVOC Contact Adhesive:  air drying contact adhesive complies with the requirements of SCAQMD Regulation 1168 for VOC content.

- Foam Tape Rolls: pre-glued black 1/8” thick Foam Tape with release backing designed for use with polyolefin insulation and is used for applications where insulation integrity needs to be maintained and polyolefin insulation cannot be readily installed.

# 2.5	JACKETING

A jacket is NOT required for INDOOR applications (installations NOT exposed to direct sunlight or weather elements), unless otherwise indicated by the specifying engineer, owner, or other agency having appropriate or legal jurisdiction.  A coating (see section 2.7) is required (jacketing is optional) for OUTDOOR applications exposed either to direct sunlight or weather elements.

# 2.6	ADHESIVES

- Field-applied Contact Adhesives.  Because of the unacceptable performance of some adhesive systems, please refer to Technical Bulletin for a list of recommended adhesives to be used in conjunction with polyolefin insulation.

# ENGINEERING NOTES:

- The recommended contact adhesives are all subject to specific service temperature ranges. The contact adhesive manufacturer should be contacted to verify correct application for service temperatures anticipated.  (The contact adhesive, when applied on joints or when applied between layers of insulation is not exposed to the extreme temperatures experienced by the reactor or piping.  Therefore, the design temperature of the adhesive will be much less demanding and must be estimated)

- It is very important that contact adhesive be allowed to flash fully prior to joining two impermeable substrates such as polyolefin insulation. Contact adhesive will not continue to flash under an impermeable substrate and will not set up properly.

- The flash time of a contact adhesive is dependent upon relative humidity and temperature. Relatively speaking, the lower the  temperature or the higher the relative humidity, the longer the time required for the contact adhesive to fully flash.

- A contact adhesive will be slightly tacky, yet dry to the touch when fully flashed.

# 2.7	COATINGS

- Insulation MUST be coated (jacket is optional) in OUTDOOR applications exposed either to direct sunlight or weather elements.  Coatings will provide the necessary protection from direct sunlight or weather elements when applied per the coating manufacturer’s installation guidelines.  The surface of the insulation must be clean and free of any dust, dirt, scale, moisture, oil and grease.  Because of the unacceptable performance of some coating systems, please refer to Technical Bulletin for a list of recommended coatings to be used in conjunction with polyolefin insulation.

# ENGINEERING NOTES:

- After long term outdoor exposure, the above coatings may weather to a light tan or yellow color.  This surface appearance will not affect the performance of the coating.

- The flexibility, impermeance, and chemical inertness of polyolefin insulation prevent strong adherence of water based latex paints. Therefore, water based latex paints are NOT recommended for coating polyolefin insulation where physical abuse is possible.

- The recommended coatings are all subject to specific application and service temperatures. The manufacturer should be contacted to verify correct utilization for anticipated temperatures.

- In some indoor applications a particular color is desired. Consult the coating manufacturer about available pigment additives. OUTDOOR applications should NOT be pigmented.

# 2.8	PIPING SYSTEMS

- Chilled water system

# ENGINEERING NOTES:

    - Dimensional stability must be taken into consideration when installing polyolefin insulation on chilled water systems. Overstuffing the insulation by 4% on all straight runs of piping is the best method for compensating for dimensional stability. With this method, the insulation will always be in a state of compression and the chance of gaps and/or butt-joint failures will be minimized.

    - Piping systems are designed to accommodate expansion and contraction. The insulation will also expand and contract. It is important to compensate for this expected pipe/insulation  movement by providing:

      - sufficient excess insulation at these points (compression fit).

      - correct sized insulation that allows movement on piping.

    - Operation temperatures below ambient and in a high humidity environment (above 90% RH) have the potential to form condensation. It is recommended that:

- the insulation wall thickness be determined after careful consideration of the lowest operating temperature and the highest ambient temperature and relative humidity.

- Tape SHOULD NOT BE USED to seal any joints since it does NOT provide an acceptable long term vapor/water barrier. See section 3.3.5 for areas that may require Foam Tape wrapping in lieu of insulation.

- Chiller equipment

- Evaporator barrels should be insulated with NOMAPLY, IMCOSHEET, THERMA-CEL SHEET. Sufficient excess insulation (¼ inch to ½ inch added to the determined dimensions) should be part of each fabricated section to allow for compression fitting of all seams.

- The insulation should be adhered to the barrel using an approved contact adhesive (see section 2.6).

- All seams and joints should be sealed using recommended joining methods (see section 3.3.3.1). This includes connecting insulated piping or any interface that occurs between insulation sections.

- Penetrations through the insulation for instrumentation ports, mechanical linkage, and miscellaneous access constraints should be sealed with a water proofing caulk that readily bonds to the insulation and to the adjacent penetration surface.

# PART 3- EXECUTION

# 3.1	WORKMANSHIP

Installation shall be performed by a qualified insulation contractor who specializes in industrial and/or commercial mechanical systems.

# 3.2	PREPARATION FOR INSTALLATION

- Apply insulation to approved and pressure tested piping and equipment systems (if applicable).

- Ensure that insulation and all mechanical piping and equipment surfaces to be insulated are clean and dry prior to installation.

- Do not apply insulation to wet or frosted surfaces.

# 3.3	INSTALLATION DETAILS

3.3.1	INSULATION OF STRAIGHT RUNS OF PIPE

- When installing NOMALOCK, IMCOLOCK, THERMA-CEL, ARCTICFLEX, (tubular):

- Snap pre-slit insulation on existing pipe or slip over new pipe PRIOR to removal of release liners.

- Firmly grasp both release liners and pull away and back, exposing factory glued seams.

- Apply firm and even pressure along the entire longitudinal seam to properly engage the pressure sensitive adhesive.

# ENGINEERING NOTE:

1.	Pressure sensitive adhesives (PSA’s) require greater pressure for proper adhesion as the temperature at time of install declines.  As a rule of thumb, beginning at 70°F, every 10°F drop in temperature requires twice as much pressure (i.e. applications at 40°F require 8 times as much pressure as applications at 70°F).  Installation is NOT recommended when the PSA seam is below 35°F.  PSA must be warmed to a temperature above 35°F before the install step.

- All insulation installed outdoors must be coated (see section 2.7).  All seam locations must be placed away from exposure to direct sunlight or weather elements, located on the lower half of the pipe.

- Seal all circumferential (butt) joints using recommended joining methods (see section 3.3.3.1).

- Compression fit insulation on continuous runs.  Install an additional 2 inches (2”) of insulation for every 6 feet (6’) of measured pipe, or 3-1/2 inches (3-1/2”) for every 10 feet (10’) of measured pipe to allow for any contraction.  Also, compression fit each segment of straight insulation meeting an elbow or tee section an additional 2 inches (2”) to compensate for the pipe/insulation combined movement. REVIEW ENGINEERING NOTE IN SECTION 2.8.

# 3.3.2	INSULATION OF VALVES, FLANGES, AND MISCELLANEOUS FITTINGS

- All fittings must be insulated at the same insulation thickness as the adjoining pipe.

- Screwed fittings must be sleeved and adhered with a one inch (minimum) overlap of the adjoining insulation.

- Bell & Spigot joints geometry will require a field fit sleeve system with a specified minimum overlap (more than one inch) of the adjoining installed pipe insulation.

- When gaps occur between the pipe insulation outside diameter (OD) and fitting insulation inside diameter (ID) a “donut” will be required.

# 3.3.2.1		TEES

- Using a very sharp knife cut a length of insulation 2 times the run length of the tee to be insulated and a second length of insulation 2 times the branch length of the tee to be insulated.

- Using the length of insulation cut to cover the run of the tee, locate the pre-glued seam at the top center, carefully cut out a half moon opening to accommodate the branch of the tee.

- Using the length of insulation cut to cover the branch length of the tee, miter the end making a concave cut to mate with the half moon opening in the run length piece.

- Pre-fit mitered pieces to insure tight fit of surfaces to be joined.  Position pieces on tee body and seal miter joints as outlined in section 3.3.3.

# 3.3.2.2		ELBOWS

- Using a very sharp knife cut 2 pieces of insulation of equal length (approximately 2 times the length of the elbow to be covered).

- Using a miter guide carefully miter cut one end of each piece of insulation to accommodate the angle of the elbow to be insulated.

- Position pre-cut pieces on elbow and pre-fit mitered ends to insure complete mating of surfaces to be joined.  Seal mitered joints as outlined in section 3.3.3.

# 3.3.2.3		MISCELLANEOUS FITTINGS

Valves, flanges, strainers, and Victaulic-type fittings are to be insulated using donuts and then covered with sheet or appropriate tubular insulation. See figures 1 and 2 for fabrication details for Victaulic-type fittings and flanges.

# 3.3.2.4	BELL & SPIGOT JOINTS

Depending on the relationship between the final installed insulation outer diameter and the outer diameter of the bell joint, one of the two field fit sleeve system options illustrated in Figures 3 and 4 should be selected. Refer to Table 1 for recommended minimum overlap for various pipe and tube sizes.

# Table 1: DETERMINATION OF MINIMUM OVERLAP

- For pipe sizes equal to or less than 6” IPS				2” overlap

- For pipe sizes equal to 7” through 12” IPS				3” overlap

- For pipe sizes equal to or greater than 13” IPS			4” overlap

# ENGINEERING NOTES:

- If multi-layer fabrication from sheet insulation is required for any of the components then additional mechanical light roughing should be done to the NON-ROUGH side in the anticipated adhesion bonding area. This will enhance the adhesive bond strength. A label is affixed to the FACTORY ROUGH SIDE of all insulation sheets. Be sure to allow the proper time interval so the previously installed layer’s adhesion is properly set.

- If tubular insulation is utilized to fabricate any components then light mechanical roughing should be done to the OUTSIDE surface of the anticipated adhesion bonding area. This will enhance the adhesive bond strength. The INSIDE of tubular insulation is sufficiently rough. Be sure to allow the proper time interval so the previous installed layer adhesion is properly set.

- For fabricated insulation sheet sleeves whose thickness exceed ¾” it is recommended that a shiplap joint be incorporated into the longitudinal joint to provide a method for alignment and better joint bonding strength.

# 3.3.3	JOINING MITERED ENDS

# 3.3.3.1	CONTACT ADHESIVE JOINING METHOD

- Coat both surfaces to be bonded with an adequate, even coat of an approved adhesive (for acceptable alternative adhesives refer to section 2.6, paragraph A).

- Follow the instructions on the contact adhesive container label for open times required prior to positioning and joining pieces.

# 3.3.4	INSULATING AT HANGERS

# 3.3.4.1	STANDARD & SPLIT HANGERS

- Size hangers to in accordance with manufacturer’s guidelines.

- Ring hangers may be sleeved with oversized tubular insulation and are to be insulated at the same insulation thickness as the adjoining pipe.

- On cold piping, when hangers are sleeved, the insulation must extend up the hanger rod at a distance equal to four times the insulation thickness.  Alternatively, Foam Tape insulation (see section 3.3.5) can be used at the hanger rod.  Wrap Foam Tape to the same insulation thickness as the adjoining pipe.

# 3.3.4.2	CLEVIS HANGERS & OTHER PIPE SUPPORTS

- Supporting devices must be used where load compression of the insulation is anticipated.  Hanger shields/saddles must be installed under all insulated piping at unistrut clamps, clevis hangers or where load compression of the insulation is anticipated.

- For piping up to 1-1/2” nominal size, wooden or plastic (polyethylene) dowels or blocks, whose length is equal to the insulation thickness, may be inserted into the insulation as support between the pipe and hanger shield/saddles.  To install dowels, cut undersized holes into the insulation such that the dowels will fit tightly.  Wooden or plastic dowels should be coated with an approved adhesive prior to their installation (for acceptable alternative adhesives refer to section 2.6 paragraph A).

- For piping larger than 1-1/2” nominal size, wooden blocks, approximately 1” wide by 3” long, are required.  Block thickness should be the same as that of the insulation.

- For best fit and long-term performance, it is best to carve out the support blocks to the contour of the pipe and hanger shield.

# 3.3.5	FOAM TAPE FOR HARD TO INSULATE AREAS

- For use in areas where it is impractical or impossible to install pipe insulation.  Convenient for wrapping valves, fittings, short runs of pipes, and hard-to-access areas.

- Surface to be covered must be cleaned free of dirt, scale, moisture, oil and grease.  Pull release liner and spiral wrap area in multiple layers with 50% overlap per layer until desired thickness is obtained.

# ENGINEERING NOTE:

It is recommended that Foam Tape material be used only on indoor applications, protected from external environment conditions.

# Text boxes

Specification for:

Nomaco All Brands Polyethylene Insulation

Page 1 of 9 (March 2016)

CSI, 3-Part Specification

Piping Insulation

Chilled Water System